Emergency sign luminaire in accordance to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.   Innovative synthetic LED edge luminaire for universal mounting (wall/ceiling/integrated ceiling mount/brackets). For mounting convenience, the luminaire consists of only 3 parts. Toollessly mountable onto the integrated quick assembly ceiling or wall mounting system. The luminaire has zero potential when dismanteled. Suitable for continuous mode or stand-by mode. Reliable planning due to a toolless and variable, on-site use of the pictograms. Set of pictograms (left, right, bottom, top) is included in the scope of delivery. LED converter with an integrated monitoring circuit for single luminaire surveillance including a 20-digit control panel with switching option.

lbl-monitoring: 
With integrated monitoring module with 20-digit addressing switch, for operation on a central power supply system. Automatic test system according to DIN EN 62034 type ER, in connection with a system of type MultiControl. Functions must be complied with:
· Integrated individual luminaire monitoring
· Integrated luminaire manager function
· Individual switchability in conjunction with RP ELS - central power supply system
lbl-material: Plastic
lbl-color: RAL 9003
maße: 34 mm x 250 mm x 174 mm
~lbl-lv-diameter:  mm

lbl-mountingMethod: Universal
lbl-protectionClass: 2
lbl-protectionRating: IP 54
lbl-impactResistanceRate: IK ≥ 3
allowed-temperature-ds: -30 °C To 40 °C celsius
allowed-temperature-bs: -30 °C To 40 °C celsius
~lbl-lv-erkennungsweite: 22m m
lbl-pictogram: Set

~lbl-lv-LeistungDauerbetrieb: 3,2 W W
~lbl-lv-LeistungBereitschaftsbetrieb: 1 W W
~lbl-lv-LichtstromNotbetrieb: 220 lm lm

~lbl-lv-EingangsspannungAC: 230 V V
~lbl-lv-Anschlussquerschnitt: 2.5 mm² mm

lbl-batterie: 

lbl-articleNumber: KSU019ML

lbl-zubehoer:
lbl-articleNumber: KME-EB, KM recessed frame with test button (SB) ABS white for KM, KSU, KSC, KMB
lbl-articleNumber: AWKSU, Wall bracket short 60x47mm, white convenient for KSU, KMU
lbl-articleNumber: 2PW-EB
lbl-articleNumber: KMBE, concrete recessed housing for KME
lbl-articleNumber: BALLPLX-KMU, Ball protection 380x280x60mm incl. fastening Plexiglas clear for KMU, KSU, KSC
lbl-articleNumber: DSA, cord suspension set 1,5m
lbl-articleNumber: KSE-MB-WS, Mounting frame with metal cover to accommodate the KSU type luminaires
lbl-articleNumber: KSE-MB-SI, Mounting frame with metal cover to accommodate the KSU type luminaires

~lbl-lv-manufacturer-addendum
