Emergency sign luminaire in accordance to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.   Innovative synthetic LED edge luminaire for universal mounting (wall/ceiling/integrated ceiling mount/brackets). For mounting convenience, the luminaire consists of only 3 parts. Toollessly mountable onto the integrated quick assembly ceiling or wall mounting system. The luminaire has zero potential when dismanteled. Suitable for continuous mode or stand-by mode. Reliable planning due to a toolless and variable, on-site use of the pictograms. Set of pictograms (left, right, bottom, top) is included in the scope of delivery. LED converter with an integrated monitoring circuit for single luminaire surveillance including a 20-digit control panel with switching option.

lbl-monitoring: 
With integrated monitoring module for operating on a Wireless Professional central monitoring system.
· Charge monitoring indicator on the luminaire
· Manual or automatic function test (free choice of test start time in the WirelessControl software)
· Manual or automatic continuous function test can be activated via the length of the luminaire’s measurement operation (free choice of test start times in the WirelessControl software)
· Automatic charge monitoring
· Deep discharge protection with restart inhibit
lbl-material: Plastic
lbl-color: RAL 9003
maße: 34 mm x 250 mm x 174 mm
~lbl-lv-diameter:  mm

lbl-mountingMethod: Universal
lbl-protectionClass: 2
lbl-protectionRating: IP 54
lbl-impactResistanceRate: IK ≥ 3
allowed-temperature-ds: -5 °C To 40 °C celsius
allowed-temperature-bs: -5 °C To 40 °C celsius
~lbl-lv-erkennungsweite: 22m m
lbl-pictogram: Set

~lbl-lv-LeistungDauerbetrieb: 3,9 W W
~lbl-lv-LeistungBereitschaftsbetrieb: 1,5 W W
~lbl-lv-LichtstromNotbetrieb: 190 lm lm

~lbl-lv-EingangsspannungAC: 230 V V
~lbl-lv-Anschlussquerschnitt: 2.5 mm² mm

lbl-batterie: LFP3233.01, {{Produkt - BatteryPerformance - BatteryTechnology (P:17:110)}} Battery

lbl-articleNumber: KSU013WL

lbl-zubehoer:
lbl-articleNumber: KME-EB, KM recessed frame with test button (SB) ABS white for KM, KSU, KSC, KMB
lbl-articleNumber: AWKSU, Wall bracket short 60x47mm, white convenient for KSU, KMU
lbl-articleNumber: 2PW-EB
lbl-articleNumber: KMBE, concrete recessed housing for KME
lbl-articleNumber: BALLPLX-KMU, Ball protection 380x280x60mm incl. fastening Plexiglas clear for KMU, KSU, KSC
lbl-articleNumber: DSA, cord suspension set 1,5m
lbl-articleNumber: KSE-MB-WS, Mounting frame with metal cover to accommodate the KSU type luminaires
lbl-articleNumber: KSE-MB-SI, Mounting frame with metal cover to accommodate the KSU type luminaires

~lbl-lv-manufacturer-addendum
