Emergency sign luminaire in accordance to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838. 
  
Innovative synthetic LED edge luminaire for universal mounting (wall/ceiling/integrated ceiling mount/brackets). For mounting convenience, the luminaire consists of only 3 parts. Toollessly mountable onto the integrated quick assembly ceiling or wall mounting system. The luminaire has zero potential when dismanteled. Suitable for continuous mode or stand-by mode. Reliable planning due to a toolless and variable, on-site use of the pictograms. Set of pictograms (left, right, bottom, top) is included in the scope of delivery. 
LED converter with an integrated monitoring circuit for single luminaire surveillance including a 20-digit control panel with switching option.

lbl-monitoring:

With integrated monitoring module for operation on a monitoring device of the Wireless Basic type.

- Time-saving configuration and commissioning as well as monitoring via Bluetooth using an Android app

- Operation in offline mode or optionally via LIGHTLINX® with versatile cloud functions

- Version with automatic test system according to DIN EN 62034 type S incl. SelfControl test button

- Test results with fault analysis (illuminant, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- Manual or automatic function test (test start time freely selectable in the WirelessBasic app)

- Configurable duration test (every 12 months)

- Automatic charge monitoring

- Deep discharge protection with restart lockout

- No-load and short-circuit shutdown of the inverter

lbl-material: Plastic

lbl-color: RAL 9003

maße: 34 mm x 250 mm x 174 mm

~lbl-lv-diameter:  mm

lbl-mountingMethod: Universal

lbl-protectionClass: 2

lbl-protectionRating: IP 54

lbl-impactResistanceRate: IK ≥ 3

allowed-temperature-ds: -5 °C To 40 °C celsius

allowed-temperature-bs: -5 °C To 40 °C celsius

~lbl-lv-erkennungsweite: 22m m

lbl-pictogram: Set

~lbl-lv-LeistungDauerbetrieb: 3,9 W W

~lbl-lv-LeistungBereitschaftsbetrieb: 1,5 W W

~lbl-lv-LichtstromNotbetrieb: 85 lm lm

~lbl-lv-EingangsspannungAC: 230 V V

~lbl-lv-Anschlussquerschnitt: 2.5 mm² mm

lbl-batterie: LFP3233.01, {{Produkt - BatteryPerformance - BatteryTechnology (P:17:110)}} Battery

lbl-articleNumber: KSU018WB

lbl-zubehoer:

lbl-articleNumber: KME-EB, KM recessed frame with test button (SB) ABS white for KM, KSU, KSC, KMB

lbl-articleNumber: AWKSU, Wall bracket short 60x47mm, white convenient for KSU, KMU

lbl-articleNumber: 2PW-EB

lbl-articleNumber: KMBE, concrete recessed housing for KME

lbl-articleNumber: BALLPLX-KMU, Ball protection 380x280x60mm incl. fastening Plexiglas clear for KMU, KSU, KSC

lbl-articleNumber: DSA, cord suspension set 1,5m

lbl-articleNumber: KSE-MB-WS, Mounting frame with metal cover to accommodate the KSU type luminaires

lbl-articleNumber: KSE-MB-SI, Mounting frame with metal cover to accommodate the KSU type luminaires

~lbl-lv-manufacturer-addendum