Emergency sign luminaire in accordance to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838. 
  
Innovative synthetic LED edge luminaire for universal mounting (wall/ceiling/integrated ceiling mount/brackets). For mounting convenience, the luminaire consists of only 3 parts. Toollessly mountable onto the integrated quick assembly ceiling or wall mounting system. The luminaire has zero potential when dismanteled. Suitable for continuous mode or stand-by mode. Reliable planning due to a toolless and variable, on-site use of the pictograms. Set of pictograms (left, right, bottom, top) is included in the scope of delivery. 
LED converter with an integrated monitoring circuit for single luminaire surveillance including a 20-digit control panel with switching option.

lbl-material: Plastic

lbl-color: RAL 9003

maße: 34 mm x 250 mm x 174 mm

~lbl-lv-diameter:  mm

lbl-mountingMethod: Universal

lbl-protectionClass: 3

lbl-protectionRating: IP 54

lbl-impactResistanceRate: IK ≥ 3

allowed-temperature-ds: -30 °C To 40 °C celsius

allowed-temperature-bs: -30 °C To 40 °C celsius

~lbl-lv-erkennungsweite: 22m m

lbl-pictogram: Set

~lbl-lv-LeistungDauerbetrieb: 2,1 W W

~lbl-lv-LeistungBereitschaftsbetrieb: 0,4 W W

~lbl-lv-EingangsspannungAC: 24 V V

~lbl-lv-Anschlussquerschnitt: 2.5 mm² mm

lbl-batterie:

lbl-articleNumber: KSU519CC

lbl-zubehoer:

lbl-articleNumber: KME-EB, KM recessed frame with test button (SB) ABS white for KM, KSU, KSC, KMB

lbl-articleNumber: AWKSU, Wall bracket short 60x47mm, white convenient for KSU, KMU

lbl-articleNumber: 2PW-EB

lbl-articleNumber: KMBE, concrete recessed housing for KME

lbl-articleNumber: BALLPLX-KMU, Ball protection 380x280x60mm incl. fastening Plexiglas clear for KMU, KSU, KSC

lbl-articleNumber: DSA, cord suspension set 1,5m

lbl-articleNumber: KSE-MB-WS, Mounting frame with metal cover to accommodate the KSU type luminaires

lbl-articleNumber: KSE-MB-SI, Mounting frame with metal cover to accommodate the KSU type luminaires

~lbl-lv-manufacturer-addendum