Four-sided LED escape sign luminaire for ceiling mounting according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838. 

Cube plastic luminaire with frameless bonnet and easy-to-mount bayonet catch. Due to the stable construction, the luminaire can also be suspended by chain or rope. 

Suitable for continuous or stand-by operation. Planning reliability thanks to logically printed pictograms according to DIN EN ISO 7010 and DIN ISO 3864 (left, right, bottom) as standard.

Monitoring:

Version with automatic test system in accordance with DIN EN 62034 type S including SelfControl test button:

- Test results with fault analysis (illuminant, charge and battery circuit) and status displays (operation, function test, continuous function test) using 3 colour LEDs

- Automatic function test (weekly)

- Automatic continuous function test (every 12 months)

- Automatic charge monitoring

- Deep discharge protection with restart inhibit

- Idling and short-circuit shutdown of inverter

Material: Plastic

Color: RAL 9003

Dimensions: 500 mm x 522 mm x 280 mm

Diameter:  mm

Mounting method: Deckenaufbau

Protection class: 2

Protection rating (IP): IP 65

Impact restistence rate IK: IK ≥ 3

Viewing distance: 50m m

Pictogram: Set

Power maintained mode: 5,6 W W

Power non-maintained mode: 0,9 W W

Battery: LFP3216-SET-2AKKU

Article number: WHGD411SC

Accessories:

Article number: LFP3216-SET-2AKKU

Brand: RP-Technik GmbH