Material: Aluminium

Color: RAL 9003

Dimensions:  mm x  mm x 113 mm

Diameter: 395 mm

lbl-mountingMethod: Universal

lbl-protectionClass: 1

lbl-protectionRating: IP 20

lbl-impactResistanceRate: IK ≥ 3

Allowed temperature DS: -5 °C to 40 °C °C

Allowed temperature BS: -5 °C to 40 °C °C

Pictogram: Nein

Power maintained mode: 28 W W

Power non-maintained mode: 2 W W

Luminous Flux Emergency Operation: 360 lm lm

Input voltage AC: 230 V V

Connection terminals: 1.5 mm² mm

Battery: LFP3245.WRLED

lbl-articleNumber: QAW403SC-BMWW

Accessories:

Brand: RP-Technik GmbH